## Slide 1
Testing HMIs, PLCs, and Protocol Gateways
in a Simulated IEC 61850 System
  Joe Stevens
  Marketing Manager
  Triangle MicroWorks
  jstevens@trianglemicroworks.com

## Slide 2
Background on Simulated IEC 61850 Systems
Examples:
  RTU/Gateway Mapping Test
  HMI Verification
  PLC Testing
Agenda

## Slide 3
Background on Simulated IEC 61850 Systems
HMI
Station Bus
Simulated IEDs
Primary
Equipment
Process Bus
RTU/Gateway
SCD File
Simulation Includes:
Communications
IED Data Models
Control Blocks
Simulated Logic

## Slide 4
Reduce Costs by Testing Earlier
Discover configuration issues earlier in the engineering process
Reduced costs by testing before acceptance testing or commissioning
Accelerate Testing Process
Test before all equipment is setup and configured
Easily change test configurations
Reduce Time with Automated Testing
Automate tests that require lots of repeatable steps
Increase test coverage with repeatable and well documented tests
Why Test With Simulated Systems?

## Slide 5
Simulated Master
RTU and Gateway Testing
SCADA System
IEC 61850
Simulated IEDs
RTU/Gateway
Device Under Test
STAT
MEAS
TRK
STAT
MEAS
PROT
STAT
MEAS
TRK
STAT
MEAS
CILO
STAT
RBRF
TRK
Data Sets
SCD File
Testing Coverage
    RTU/Gateway Configuration
    Control Mapping
    Report Mapping
    Value, Time, Quality

## Slide 6
Simulated Master
Gateway Example
SCADA System
IEC 104
Protocol Gateway
Create Mapping Results
  XCBR.Pos.stVal  M104.T3.P13
  MMXU.A.phsA.cVal  M104.T13.P30
  CILO.EnaCls.stVal  M104.T1.P34
  CSWI.Pos.stVal  M104.T3.P31
  MMXU.PhV.phsA.cVal  M104.T13.P33
  CILO.EnaOpn.stVal  M104.T1.P35
1) XCBR.Pos.stVal = Open -> Closed
2) MMXU.A.phsA.cVal = 0 -> 100
3) CILO.EnaCls.stVal = 0 -> 1
Create Events
IEC 61850
Record
Results
Simulated
IEDs

## Slide 7
HMI Testing
Device Under Test
Alarm Events
Statuses
Measurements
Control Requests
Simulated IEDs
SCD File
Testing Coverage
    HMI Configuration
    Controls
    Alarms/Events
    Measurements
HMI
Test Cases
Tests

## Slide 8
HMI Example
Step Through
Test Cases
Simulated
IEDs
Reports
Controls
Operator
Test Case | Objects Tested | Test Values
1) Alarm Event | MMXU.A.phsA.cVal | 1,000 -> 1,200 A
2) Fault Event | PDIS.Op XCBR.Pos | False -> True Closed -> Open
3) Control Request | CSWI.Pos.stVal | Open -> Closed
HMI
Results
Transformer Alarm
Distance Fault
Breaker Control
Record Results

## Slide 9
PLC Testing
Simulated IEDs
Device Under Test
Testing Coverage
    PLC Configuration
    Verify logic/algorithms
    Verify mappings
PLC
Initial state to setup test
Sequence of states for test case
Simulated IEDs
Test States
SCD File
Tests

## Slide 10
PLC Example
Simulated IEDs
PLC
States for
Test Case
Test Step | Objects Tested | Test Values
1) Bus Energized | MMXU.PhV.phsA.cVal | 0 -> 220kV
2) Breaker Interlock | CILO.EnaOpn.stVal | False -> True
3) Control Request | CSWI.Pos.stVal | Open -> Closed
Reports
Controls
GOOSE
Results
Bus Energized
Interlock
Breaker Closed

## Slide 11
  Joe Stevens
  Marketing Manager
  Triangle MicroWorks
  jstevens@trianglemicroworks.com
Find Issues Earlier
Discover issues at an earlier stage
Increase Test Coverage
Test devices in realistic system conditions
Take Advantage of IEC 61850
Leverage the value of the system configuration approach (SCD File)
Key Takeaways